Jamnagar Refinery Complex – Reliance Petroleum Ltd

Security Automation System

Executive Summary of Evaluation of Proposals

8.12.99

General

- Two proposals were submitted to the final phase:

- Magal’s proposal with MLL equipment

- Johnson Control with Cardax equipment.

- For detailed technical comparison, see in the attached tables.

- As an output of the detailed comparison table following is overall gradation:

| Vendor | Access Control | CCTV |
| --- | --- | --- |
| Magal | 94.8 | 100 |
| Johnson Control | 75.35 | 79 |

Access Control

- The technical tabulation compares in detail the specification of units and their features, without taking into consideration all integration aspects. From the vendors’ meetings and documentation submitted by the vendors, differences in quality of the offers and the likely performance of the system is expected to be much larger than can be seen in the comparison table. 
Johnson Control’s system as offered, may be able to perform only as a standard access controls system. Johnson Control proposal for most of the custom-built  requirements requested by RPL (Bus operation, Black list, portable readers etc.), is:

- Unacceptable  - The solution for Bus operation does not answer even basic access control requirements.

- Unclear  - Recognition Systems, the manufacturer of HandKey, promised Cardax helping them with information, enabling them to try and solve the black list requirements. No concrete solution is offered.

- Partial  - After we rejected the portable reader, due to size and weight, a new idea was raised, more details were promised but never arrived.

Subsequent to the meeting Johnson Control have sent a message that they will write special application to meet the custom-built requirements, however there are no details available.

- Concerning the integration with other systems, Johnson Control could not ensure integration with the perimeter system (saying that only if it is on OPC standard, integration can be achieved). Even with their own CCTV system they couldn’t submit a detailed scheme (description was promised and never arrived). Magal’s integration with CCTV is through SMS software, which Johnson Control couldn’t offer.

- Johnson Control does not have higher level software of SMS (Security Management System). They say that their Access Control software is good enough to give these services to the system. We expect future problems in integration and operation mainly when the perimeter system will be implemented.

- Magal offered a complete solution to all access control requirements. They built prototypes for all RPL’s customized equipment (portable readers) and showed us demonstration of all specially required applications (bus operation, black list, time attendance etc..). Every question was answered in the most open way and most of the required documentation was submitted on time.

# CCTV System

- Both companies offered good quality cameras meeting most of RPL’s requirements.

- Magal has offered Elbex cameras which have some special unique features, improving CCTV system’s performance as following:

- PIP (Picture in Picture) range finder which is mini B/W wide angle camera displaying the entire field of view, enabling the observer “easy recognition” of the camera positioning, particularly whenever the zoom lens is set to telephoto.

- The camera, its fully equipped outdoor housing, the PTZ control and all other accessories, is one integrated heavy-duty unit.

- The offered units are already fully integrated with the communication network (Video, configuration data, PTZ data, audio) and everything is done on a single coaxial cable.

- The unit is designed specially for hot climate areas and has good temperature isolation layers, as well as very sophisticated cooling system.

- As Magal is offering, and demonstrated us, a complete solution for CCTV system which is over qualified (according to RPL’s requirements), this may have cost effect on their proposal. If price is too high, maybe other options should be taken in consideration.

- The cameras offered by Johnson Control, based on Molynx equipment, are of good quality but mainly based on standard components with no special additional value. From the specification submitted, the camera offered may have problems in hot climate areas, as the offered unit cannot handle a blower (fan).

- The computerized transmission, recording and control of the CCTV system, offered by Johnson Control, as was presented to us (MV2000), has very poor in picture quality (resolution and number of frames per second).  Johnson Control realized this problem and promised to comeback with a better solution. They informed us later that there is a better system but couldn’t send us any information or documentation.

- Johnson Control couldn’t offer thermal long-range surveillance system for the SPM.

- Johnson Control didn’t offer VMD (Video Motion Detector) as requested by RPL.

- Johnson Control offered a simple SVGA projector (front projection) instead of Video wall as required by RPL. This solution requires dark room and cannot be accepted for the control center. Subsequently they have quoted for a Video Wall but no details are available as yet. Magal has offered Barco made Video Wall. Additional information is requested to enable selection of model.

# Communication System

- Both offers are giving good solutions for the special requirements of the “Security Net”. Both vendors understood well RPL’s requirements and based their offers on top quality, “state of the art” equipment.

- According to Technical specifications of the Intel Switchers offered by Johnson Control, this equipment may not be installed and operated outdoors (or in non air-conditioned area). This can cause a problem in at least one switch now, and any future outdoor switch.

## General Comments

- Johnson Control‘s offer is found to be technically inferior. Johnson Control is well known international company in BMS (Building Management System), however their approach to this job was found to be poor. Adequate homework was not done and number of technical issues could not be answered or backed up.  Johnson Control is contributing no value of its own to the project as they are not supplying any software or hardware. Johnson Control is handling only prime contracting, management with a consortium with Cardax and Molynx. As they do not have any specific experience in large-scale outdoor security projects, they have to depend totally on their chosen subcontractors. The consortium is made especially for this project, future support after project completion, is not clear.

The actual proposal of Johnson Control still has a lot of “dark holes” where solutions are not yet achieved, or not yet clear. There are still some issues that can be considered as “high risk” (from technical and cost aspects) for both parties (Owner and Vendor).

- We were very impressed with the approach of Magal during preparation of their proposal. All Customized requirements were seriously analyzed, prototypes of special equipment were built and tested as well as software modifications were written and presented. Magal gave us the confidence that they have well understood the RPL requirements and all systems are expected to work properly on site.

# Recommendation

- As can clearly be understood from this document our recommendation, based on all technical aspects, is to choose Magal’s proposal not only as the preferred one, but as the only proposal that can ensure proper implementation of the project  without  taking any risk .

- Magal, executing this part of the project, can ensure smooth (from technical point of view) and efficient (from economic point of view) integration with the PIDS (Perimeter Intrusion Detection System) planned as the next step of RPL’s security project.