: Comparison of Intrusion Detection Systems for MTF / Marine area :

| No | System | Comparative features (Advantages / Disadvantages ) | Consultant’s Recommendation |
| --- | --- | --- | --- |
| 1 | Taut wire System (Stainless Steel) | - Minimum power and communication cabling, no additional lighting. - Intrusion Detection rate very high - Very less False alarm - Long life - Standardized system - Identical to Refinery Taut wire except SS - Physical deterrence | Technically Recommended. |
| 2 | Microphonic Cable | - High rate of False alarms, especially due to wind - Welded mesh on compound wall required to mount microphonic cable - Stainless steel mesh to avoid frequent replacement. - Physical deterrence | Technically not suitable. Not Recommended. |
| 3 | Infra-Red System | - Straight zones of 50 m required to mount transmitters and receivers. - Power supply required at each 50m zones - High rate of False alarms - Requires very strong and stable pillars for mounting IR posts - No Physical deterrence | Technically not suitable. Not Recommended. |
| 4 | # Buried Cable | - Requires sterilised land strip of min. 6 m around the boundary, which is not available in MTF and pipeway to jetty. - Inconsistent performance due to changes in magnetic field caused by presence of water (Rain, Running water, accumulated water etc.) - Liquid carrying pipe crossings can not be tolerated - Overhead power cables affect the performance - Micro grading (Concrete) is required to clear the surface water. - No physical deterrence | Technically not suitable. Not Recommended. |
| 5 | Video Motion Detection | - Approximately 230 nos. cameras are required to cover the perimeter. - Requires additional lighting around the perimeter - Requires additional fibre optic cabling around to perimeter - Bad weather like Rain, Fog makes cameras redundant - Requires explosion proof housing for camera for MTF areas - No physical deterrence. | Technically not suitable. Not Recommended. |