## Surveillance System
Sl.No. | Technical feature | Equipment offered | Weight | Magal Replies | Grade | Johnson Controls / Molynx Replies | Grade | Remarks
1.00 | High resolution color CCD camera |  | 20% |  | 100%x20 =20 |  | 80%x20= 16
1.01 | CCD size | 1/2" / 1/3" / 1/4" |  | 1/2” |  | 1/3" |  | Both acceptable
1.02 | Pixel array (H x V, pixels) |  |  | 752 x 582 |  | 752 (H) X 582 (V)
1.03 | Resolution (horizontal TV lines) |  |  | 470 |  | 470
1.04 | Usable sensitivity at F1.2 (lux) |  |  | 1 Lux-100000 Lux |  | 1Lux(max. not specified)
1.05 | Automatic Gain Control | Yes / No |  | Yes |  | Yes
1.06 | Back Light Compensation | Yes / No |  | Yes |  | Yes
1.07 | Digital Signal Processing | Yes / No |  | Yes |  | Yes
1.08 | Electronic Shutter Control | Yes / No |  | Yes |  | Yes
1.09 | Signal to Noise ratio with AGC off (>db) |  |  | >47 db |  | 46 dB
1.10 | Auto White Balance | Yes / No |  | Yes |  | Yes
1.11 | Auto White Balance, range (in degree K) |  |  | 3100 -7000 K degrees |  | 3200-8000
1.12 | Lens mount | C / CS / Universal |  | C built in |  | Universal
1.13 | Mount provision (1/4" UNC-20 screw) | Top / Bottom / Both |  | Both |  | Both
1.14 | Input supply (volts) | AC / DC Voltage _____ |  | AC Voltage 24V / 230V- 50 Hz_____ |  | AC Voltage 24V / 230V- 50 Hz_____
1.15 | Synchronisation | Line Lock (AC) / Crystal-Lock (DC) / None / Any Other (pls. Specify) |  | Frame lock (external) |  | Line Lock (AC)
1.16 | Power Consumption (max, W) |  |  | 30W including all accessories |  | 6 W max
1.17 | Power indicator LED | Yes / No |  | no |  | Yes
1.18 | Make of camera |  |  | Elbex |  | MOLYNX
1.19 | Make of CCD chip |  |  | sony |  | SONY
1.20 | Certifications / Approvals | UL / CE / Any other |  | CE |  | CE
1.21 | Settings controlable remotely | Yes / No |  | Yes |  | Yes
1.22 | If yes, specify communication format | RS232 / RS422 / RS485 / Any other (pls. specify) |  | RS-422 |  | RS485
1.23 | Color-by-day, B/W-by-night option offered ? | Yes / No |  | Yes |  | No |  | Required, big advantage during dark hours.
1.24 | Operating Temperature (deg. C) |  |  | -' 35°C - +50°C |  | -10° - +50°C
1.25 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) |  | No |  | No |  | Elbex has advanced PIP (picture in picture) feature
2.00 | Fixed focal length auto iris lens |  | 5% |  | 100%x5=5 |  | 100%x5=5
2.01 | Format of lens | 1/2" / 1/3" / Any other (pls. specify) |  | 1/2" |  | 1/2" / 1/3"
2.02 | Video drive iris | Yes / No |  | No |  | No
2.03 | Type of mount | C / CS |  | C |  | CS
2.04 | Iris range (f-stops) |  |  | - |  | 125
2.05 | Lens offered (focal length, mm) | 4 / 6 / 8 / 10 / 12 / Any other (pls. specify) |  | 6-12 f 1.4 |  | 6-15mm Verifocal, variable
2.06 | 4-pin connector | Yes / No |  | Yes |  | Yes
2.07 | Make |  |  | Elbex |  | MOLYNX
2.08 | Certifications / Approvals | UL / CE / Any other |  | CE
2.09 | Operating Temperature (deg. C) |  |  |  |  | -10° - +50°C
2.10 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) |  | No |  | No
3.00 | Mororised Zoom Lens with Auto Iris |  | 10% |  | 100%x10=10 |  | 100%x10=10
3.01 | Format of lens | 1/2" / 1/3" / Any other (pls. specify) |  | 1/2" |  | 1/2"
3.02 | Video drive iris | Yes / No |  | Yes |  | Yes
3.03 | Type of mount | C / CS |  | C |  | C
3.04 | Does the lens support presets ? | Yes / No |  | Yes |  | Yes
3.05 | Focal length range of lens offered (mm) | 8-80 / 10-100 / 8-160 / 10-200 / Any other (please specify) |  | 10-200mm |  | 10-200mm |  | Offer for 10-200 should be certified with JC
3.06 | Minimum object distance (m) | Pls. specify for each model of lens offered |  | 1.2 m |  | 1 METER
3.07 | Zooming speed (sec) | Pls. specify for each model of lens offered |  | 3-4 sec |  | 3-5 Sec
3.08 | Focus speed (sec) | Pls. specify for each model of lens offered |  | 3-4 sec |  | 3-5 Sec
3.09 | 4-pin connector | Yes / No |  | Yes |  | Yes
3.10 | Make |  |  | Elbex |  | MOLYNX
3.11 | Certifications / Approvals | UL / CE / Any other |  | CE
3.12 | Operating Temperature (deg. C) |  |  | -85 |  | -10° - +50°C
3.13 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) |  | No |  | No
4.00 | Weatherproof camera housing / enclosure |  | 10% |  | 100%x10=10 |  | 80%x10=8
4.01 | Opening mechanism | Hinge at front / Hinge at rear / Any other (pls. specify) |  | Hinge at top |  | Hinge at front
4.02 | Adjustable camera mounting sled / plate | Yes / No |  | Yes |  | Yes
4.03 | Lockable with padlock | Yes / No |  | Yes |  | No |  | Additional security measure available with Magal
4.04 | Tamper alarm | Yes / No |  | Yes |  | No |  | Additional security measure available with Magal
4.05 | Blower | Yes / No |  | Yes |  | No |  | Critical feature , required in hot areas
4.06 | Defroster / heater | Yes / No |  | Yes |  | Yes
4.07 | Sun-shroud | Yes / No |  | Yes |  | Yes
4.08 | Wash (optional) | Yes / No |  | Optional |  | Yes
4.09 | Wiper (optional) | Yes / No |  | Optional |  | Yes (included)
4.10 | Can wiper be retro-fitted at site | Yes / No |  | No |  | No
4.11 | IP rating |  |  | IP 66 |  | IP 66
4.12 | Cable entry provisions (type and nos.) |  |  | sleev thre |  | IP 66 Gland x 3 x 1 blancking hole
4.13 | Fabrication material |  |  | Polycarbonate filled with polyurethane foam serrounded by silicon rubber |  | Aluminium
4.14 | Finish |  |  | N/A |  | Epoxy Coated
4.15 | Window dimensions (H x W, mm) |  |  | 82 x 95 mm |  | 100mm x 75mm
4.16 | Window construction | (type of material, thickness, etc.) |  | Glass, 4mm |  | Tough Glass
4.17 | Make |  |  | Elbex |  | MOLYNX
4.18 | Certifications / Approvals | UL / CE / Any other |  | CE |  | CE
4.19 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) |  | No |  | No
5.00 | Explosion proof camera enclosure |  | 5% |  | 100%x5=5 |  | 100%x5=5
5.01 | CELENEC standard complied with | Ex / d / IIB / IIC / T6 |  | Ex / d / IIB / IIC / T6 |  | Ex / d / IIB / T6
5.02 | National Electrical Code complied with | Class I, Div. I, Group C & D / Class II, Div. I, Groups E, F & G / Any other (pls. specify) |  | Class I |  | Class I, Div. I, Group C & D / Class II, Div. I, Groups E, F & G / Any other (pls. specify)
5.03 | Is it BASEEFA certified ? | Yes / No |  | No |  | Yes
5.04 | Capable of housing receiver / driver unit | Yes / No |  | Yes |  | Yes
5.05 | Defroster / heater | Yes / No |  | Yes |  | Yes
5.06 | Sun-shroud | Yes / No |  | Yes |  | Yes
5.07 | IP rating |  |  | IP67 |  | IP 67
5.08 | Fabrication material |  |  | Aluminum |  | Aluminium
5.09 | Finish |  |  | Powder Paint |  | Epoxy coated
5.10 | Window dimensions (mm) |  |  | 90 mm |  | 5 inch diameter
5.11 | Window construction | (type of material, thickness, etc.) |  | Glass 10mm |  | Tough Glass
5.12 | Wiper (optional) | Yes / No |  | Yes |  | Yes
5.13 | Make |  |  | Pelco |  | MOLYNX
5.14 | Certifications / Approvals | UL / CE / Any other |  | CE / EN ISO9002 |  | CE
5.15 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) |  | No |  | Yes (Blower Not Available)
6.00 | Pan and tilt drive unit |  | 10% |  | 100%x10=10 |  | 100%x10=10
6.01 | Variable speed | Yes / No |  | Yes |  | Yes |  | Magal's option is required
6.02 | Presets | Yes / No |  | Yes |  | Yes
6.03 | Number of presets |  |  | 99 |  | 99
6.04 | 360 degree pan | Yes / No |  | Yes - continuos |  | 365 deg PAN
6.05 | 100% Duty Cycle in pan mode | Yes / No |  | Yes |  | Yes
6.06 | Inverted mount option | Yes / No |  | Yes |  | Yes
6.07 | Pan speed range (degree / second) |  |  | 6-30 deg/sec |  | 0-48 deg/sec
6.08 | Tilt range from horizontal (degrees) |  |  | ±90 degrees |  | +90 deg
6.09 | Tilt speed (degree / second) |  |  | 6-30 deg/sec |  | 0-24 deg/sec
6.10 | Maximum load (kgs) |  |  | NA |  | 12Kg
6.11 | IP Rating |  |  | IP 66 |  | IP 66
6.12 | Input voltage (volts) | AC / DC Voltage _____ |  | 24AC/ 230 VAC |  | DC Voltage 24V DC
6.13 | Power Consumption (max, W) |  |  | 8 W
6.14 | Make |  |  | Elbex |  | MOLYNX
6.15 | Certifications / Approvals | UL / CE / Any other |  | CE |  | CE
6.16 | Operating Temperature (deg. C) |  |  | (-)35 - +60°C |  | -20° TO +60°C
6.17 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) |  | No |  | No
7.00 | Explosion proof Pan and tilt drive unit |  | 5% |  | 100%x5=5 |  | 100%x5=5
7.01 | Variable speed | Yes / No |  | Optional |  | No
7.02 | Presets | Yes / No |  | Yes |  | Yes
7.03 | Number of presets |  |  | 99 |  | 99
7.04 | National Electrical Code complied with | Class I, Div. I, Group C & D / Class II, Div. I, Groups E, F & G / Any other (pls. specify) |  | Class I |  | Class I, Div. I, Group C & D / Class II, Div. I, Groups E, F & G
7.05 | CELENEC standard complied with | Ex / d / IIB / IIC / T6 |  | Ex / d / IIB / IIC / T6 |  | Ex / d / IIB / T6
7.06 | Is it BASEEFA certified ? | Yes / No |  | No |  | Yes
7.07 | Pan speed (degree / second) |  |  | 6 degrees/second |  | 6 deg/sec
7.08 | Tilt range from horizontal (degrees) |  |  | ±90 degrees |  | +90 deg
7.09 | Tilt Speed (degree / second) |  |  | 6 degrees/second |  | 3 deg /sec
7.10 | Maximum load (kgs) |  |  | 25 kg |  | 50 Kg
7.11 | IP Rating |  |  | IP 67 |  | IP 67
7.12 | Input voltage (volts) | AC / DC Voltage _____ |  | 24 AC |  | AC
7.13 | Power Consumption (max, W) |  |  | 8 W |  | 60 W
7.14 | Make |  |  | Pelco |  | MOLYNX
7.15 | Certifications / Approvals | UL / CE / Any other |  | CE |  | CE
7.16 | Operating Temperature (deg. C) |  |  | - 10°C - +60°C |  | -20° TO +60°C
7.17 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) |  | No |  | No
8.00 | Camera mount |  | 5% |  | 100%x5=5 |  | 100%x5=5
8.01 | Types of mounts available | tower / wall / ceiling / corner / pole / any other |  | wall,(pole, ceiling) |  | tower / wall / ceiling |  | Should be approved by Magal
8.02 | All accessories for tower top mounting included? | Yes / No |  | Yes |  | Yes |  | Should be approved by Magal
8.03 | Maximum load (kgs) |  |  | 25 kg |  | 40 Kg ( 100 Kg for Flameproof PTZ )
8.04 | Adjustable head | Yes / No |  | Yes |  | No
8.05 | Make |  |  | Elbex |  | MOLYNX
8.06 | Certifications / Approvals | UL / CE / Any other |  | CE |  | CE
8.07 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) |  | No |  | No
9.00 | Telemetry receiver / driver unit |  | 10% |  | 100%x10=10 |  | 100%x10=10
9.01 | Functions controlled | Pan / Tilt / Zoom / Focus / Iris / Speed / Wash / Wipe / Blower / Heater / Any other (pls. specify) |  | Pan / Tilt / Zoom / Focus /Speed / Wash / Wipe / Blower / Heater / Presets |  | Pan / Tilt / Zoom / Focus / Iris / Speed / Wash / Wipe / 17 Function
9.02 | External | Yes / No |  | Yes |  | Yes
9.03 | IP rating (if external) |  |  | IP 66 |  | IP 66
9.04 | Communication with matrix | RS232 / 422 / 485 / proprietary / Any other (pls. specify) |  | FTT10 |  | RS 485
9.05 | Number of presets |  |  | 99 |  | 99 |  | Magal's no. should be checked
9.06 | Preset tours | Yes ( ___ nos.) / No |  | Yes |  | Yes
9.07 | Preset sequencing | Yes ( ___ nos.) / No |  | Yes |  | Yes
9.08 | Alarm Inputs | Yes ( ___ nos.) / No |  | No |  | No
9.09 | Alarm Outputs | Yes ( ___ nos.) / No |  | No |  | No
9.10 | Shortest route to preset position | Yes / No |  | Yes |  | Yes
9.11 | Fabrication |  |  | Plastic |  | N.A.
9.12 | Input voltage (volts) | AC / DC Voltage _____ |  | 240AC |  | 240 AC
9.13 | Power consumption (max, W) |  |  | 240V- 5A |  | 20 VA Exculding housing
9.14 | Capable to supply power to camera and all accessories offered ? | Yes / No |  | Yes |  | Yes
9.15 | Lockable with padlock | Yes / No |  | No |  | No
9.16 | Make |  |  | Elbex |  | MOLYNX
9.17 | Certifications / Approvals | UL / CE / Any other |  | UL / CE |  | CE
9.18 | Operating Temperature (deg. C) |  |  | - 20°C - +60°C |  | -20° TO +60°C
9.19 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) |  | No |  | No
10.00 | Integrated Dome Type Camera with PTZ |  | 5% |  | 100%x5=5 |  | 100%x5=5
10.01 | CCD size | 1/2" / 1/3" / 1/4" |  | 1/2" |  | 1/3" |  | Both accepted
10.02 | Pixel array (H x V, pixels) |  |  | 752 x 582 |  | 752 x 582
10.03 | Resolution (horizontal TV lines) |  |  | 470 |  | 450 TVL
10.04 | Usable sensitivity at F1.2 (lux) |  |  | 1 Lux |  | 3.7 Lux |  | JC: Lux level is very high
10.05 | Automatic Gain Control | Yes / No |  | Yes |  | Yes
10.06 | Back Light Compensation | Yes / No |  | Yes |  | Yes
10.07 | Digital Signal Processing | Yes / No |  | Yes |  | Yes
10.08 | Electronic Shutter Control | Yes / No |  | Yes |  | Yes
10.09 | Signal to Noise ratio with AGC off (>db) |  |  | > 48 db |  | 45 dB
10.10 | Auto White Balance | Yes / No |  | Yes |  | Yes
10.11 | Auto White Balance, range (in degree K) |  |  | 3100-7000 K degrees |  | 3200 to 8000K
10.12 | Input supply (volts) | AC / DC Voltage _____ |  | 240VAC / 15VDC |  | 24 DC Voltage _____
10.13 | Synchronisation | Line Lock (AC) / Crystal-Lock (DC) / None / Any Other (pls. Specify) |  | Frame Lock |  | Crystal-Lock (DC) / None
10.14 | Power Consumption (max, W) |  |  | 20 W |  | 31 W
10.15 | Make |  |  | Elbex |  | VIDEOMECH
10.16 | Make of CCD chip |  |  | Sony |  | SONY
10.17 | Focal length range of lens (mm) |  |  | 8 – 80 mm |  | 5.8 to 58mm
10.18 | Zooming speed (sec) |  |  | 5 sec |  | 3 - 5 sec
10.19 | Focus speed (sec) |  |  | 3 sec |  | 3 - 5 sec
10.20 | Variable speed Pan & Tilt | Yes / No |  | Yes |  | Yes |  | Vriable speed required
10.21 | Number of presets |  |  | 99 |  | 99
10.22 | 100% Duty Cycle in pan mode | Yes / No |  | Yes |  | Yes
10.23 | 360 degree pan | Yes / No |  | Yes |  | Yes
10.24 | Pan speed range (degree / second) |  |  | 6-35 degree/second |  | 0 to 240 deg/sec
10.25 | Tilt range from horizontal (degrees) |  |  | ±90 degrees |  | 5 to 90 deg
10.26 | Tilt Speed (degree / second) |  |  | 6 -35 degrees/second |  | 0 to 120 deg/sec
10.27 | Blower | Yes / No |  | Optional |  | No
10.28 | Defroster / heater | Yes / No |  | Optional |  | No
10.29 | IP Rating |  |  | IP 66 |  | IP 20 |  | JC: Can be used only indoor
10.30 | Fabrication |  |  | Aluminum + Plastic |  | N.A
10.31 | Finish |  |  | White |  | Polycarbonate
10.32 | Type of glass |  |  | Plastic |  | N.A
10.33 | Certifications / Approvals | UL / CE / Any other |  | CE
10.34 | Operating Temperature (deg. C) |  |  | -' 30°C - +50°C |  | 0 to 45 deg
11.00 | Long Range Thermal Imaging Camera |  | 15% |  | 100%x15=15 | NOT OFFERED | 0%x15=0
11.01 | Field of regards - horizontal (deg.) |  |  | Fixed
11.02 | Field of regards - vertical (deg.) |  |  | Fixed
11.03 | Angular velocity (rad / sec) |  |  | Not Applicable
11.04 | Angular reporting accuracy (deg.) |  |  | Not Applicable
11.05 | Dual Field of View (FOV) lens | Yes / No |  | Yes
11.06 | Wide field of view - horizontal (deg.) |  |  | 3.2 degrees
11.07 | Wide field of view - vertical (deg.) |  |  | 2.6 degrees
11.08 | Narrow field of view - horizontal (deg.) |  |  | 1.2 degrees
11.09 | Narrow field of view - vertical (deg.) |  |  | 0.9 degrees
11.10 | Forward Looking Infra-Red Sensor type |  |  | Not Applicable
11.11 | Focal Plane Array (H x V, pixel)
11.12 | PAL Video Output | Yes / No |  | Yes
11.13 | Laser Range Finder (optional) | Yes / No |  | No
11.14 | Range (,000 m) |  |  | Up to 12,000 m
11.15 | Range accuracy (+/- m)
11.16 | Intruder Detection Range (6m wide moving object), Wide FOV (,000 m) |  |  | 4 km
11.17 | Intruder Detection Range (6m wide moving object), Narrow FOV (,000 m) |  |  | 11km
11.18 | Operating Temperature (deg. C) |  |  | MIL -STD-910
11.19 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) |  | No
| Total Grade of CCTV |  |  |  | 100 |  | 79 | VideoWall is required but is not included in this table. JC proposal for front projector is not acceptable. JC have quated for video wall. Details not available.

## Access Control System
Sl.No. | Technical feature | Equipment offered | Magal / MLL Replies | Johnson Controls / Cardax Replies | Remarks
1.00 | System Software & General
1.01 | Windows NT Operating System | Yes / No | Yes. | Yes
1.02 | Max. No. of card holders | (offered ______ / expandable _______ ) | Offered: 40,000 Expandable: 100,000 | (offered 10,000 / expandable 900,000)
1.03 | Max. No. of readers | (offered ______ / expandable _______ ) | Offered: 400 | (offered 442 / expandable 4000 )
1.04 | Max. No. of zones / areas | (offered ______ / expandable _______ ) | Offered: 64 Expandable:128 | (offered 1840 / expandable 4,000)
1.05 | Max. Alarm inputs | (offered ______ / expandable _______ ) | Not limited | (offered 1086 / expandable 30,000)
1.06 | Max. Alarm outputs | (offered ______ / expandable _______ ) | Not limited: | (offered 362 / expandable 20,000)
1.07 | Data fields per user |  | 30 | 64
1.08 | Image fields per user |  | 3 | 3
1.09 | Notes field per user ? | Yes / No | Yes | Yes
1.10 | Provision for multiple card issue levels for same card no.? If yes, how many? |  | Yes. 5 issue levels the same card number. | 15
1.11 | Max. No. of individual operators | (offered ______ / expandable _______ ) | Not limited | (offered 500/ expandable 500 )
1.12 | Max. No. of operators logged on simultaneously | (offered ______ / expandable _______ ) | Not limited | (offered 6 / expandable 20 )
1.13 | Provision for pre-defined action plans for various emergency conditions ? If yes how many? |  | Not limited | Yes. There is no limit imposed by the Cardax system
1.14 | Multiple alarm levels in terms of criticality? If yes, how many? |  | Yes. Unlimited number of critical alarm levels | 10
1.15 | Log of all operator events? | Complete / Partial / None | Complete | Complete
1.16 | Anti-passback | Global / Zonal / Both / None | The system enables global & local anti pass-back | Global and Zonal
1.17 | Auto-forgive for anti-passback | Card wise / Zone Wise / All / None | Card wise, Site wise | Card wise and Zone Wise
1.18 | Modes of access definable for each unit (please specify) |  | Closed, Access Controlled, Free access, Free passage (Free passage is not restricted by time zones) | Secure (no PIN), Secure (with PIN), pending, free access, PIN only, dual authorisation, escort
1.19 | No. of public holidays supported |  | Not limited | 30
1.20 | Holidays definable for full year | Yes / No | Yes | Yes
1.21 | No. of work timetables definable |  | Not limited | No limit imposed by the Cardax system
1.22 | Is it possible to alter specific details of a group of users at a time e.g. change access level, department, add another access zone, etc ? | Yes / No | Yes | Yes / No
1.23 | In-built guard tour system | Yes / No |  | Yes
1.24 | If yes, does it support other inputs apart from card readers such as key-switch, push-button, etc for tour points ? | Yes / No |  | Yes
1.25 | No. of points of each tour |  |  | No limit imposed by the Cardax system
1.26 | No. of guard tours definable |  |  | 50
1.27 | No. of guard tours running concurrently |  |  | 20
1.28 | Guard tour initiation | Time based / Operator triggered |  | Operator triggered (Allows flexibility for guards to begin a tour a slightly differing times)
1.29 | Is it possible to have an operator to monitor and process alarms only ? | Yes / No | Yes | Yes
1.30 | Is the above definable operator-wise or workstation-wise ? |  | Operator wise (According to the operator’s authorization) | Operator-wise
1.31 | Database format |  | SQL 7 | SQL Server 7
1.32 | Time and attendance - in-built ? | Yes / No | Yes | Yes
1.33 | User customisable reports ? | Yes / No | Yes | Yes
1.34 | All reports available in ASCII format ? |  | ASCII and other formats such as: Exell RTF etc) | Yes
1.35 | Are all the alarm inputs balanced ? |  | What is the meaning of balanced inputs? | Yes
1.36 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) | No | Yes. Refer to Deviations document
2.00 | Field Controller
2.01 | Intelligent to handle user verification locally | Yes / No | Yes | Yes
2.02 | Type of microprocessor |  | 80 C 32 | Intel 386
2.03 | Type of memory |  | Static Ram 128K byte upgrade: to 512 Kbytes | Flash
2.04 | 32-bit processing | Yes / No | 8- bit processing | Yes
2.05 | Supports digital audio / video | Yes / No | No | Yes
2.06 | Max. no. of Controllers supported | (offered ______ / expandable _______ ) | 256(RS485 communication). The number of controllers in TCP/IP communication is not limited. | (offered 115 / expandable 500 )
2.07 | Field controller memory - users | (offered ______ / expandable _______ ) | 40000 | (offered 10,000 / expandable 200,000 )
2.08 | Field controller memory - events | (offered ______ / expandable _______ ) | 4000 | (offered 10,000 / expandable 25,000 )
2.09 | Field controller memory retention |  | 4000 | Permanently stored in the flash memory technology which does not require a back up battery.
2.10 | Type of Communication between Controller and Host server | RS232 / RS422 / RS485 / TCP/IP / Any other (pls. specify) | RS485 , Dial modem, TCP/IP , RS232 | TCP/IP, (RS232 in future versions)
2.11 | Communication encrypted between Controller and Host server | Yes / No | Yes | Yes
2.12 | Communication encryption | 32-bit / 64-bit / any other (pls. specify) | Other propriety method | 64-bit rolling key
2.13 | Dial-up communication between Controller and Host server supported ? | Yes / No | Yes | Yes
2.14 | Is it possible for the Controller to fall-back to dial-up communications in case of main communication channel failure ? | Yes / No | Yes | Yes
2.15 | Can controller initiate dial-up to Server ? | Yes / No | Yes | Yes
2.16 | Is it possible to stop the controller from functioning if the controller memory fills up during communication failure between server and controller ? | Yes / No | Yes | No
2.17 | In-built Real Time Clock |  | Yes | Yes
2.18 | All events time and date stamped | Yes / No | Yes | Yes
2.19 | Frequency of clock synchronisation with Host server |  | Programmable | Hourly
2.20 | Card technologies supported | Barcode / Hi-Co Magnetic Stripe / Proximity / Long Range Proximity / Contact Less Smart Cards | Barcode, Hi-co magnetic stripe, Proximity, Long range Proximity, Contact Less Smart Cards | Barcode / Hi-Co Magnetic Stripe / Proximity / Long Range Proximity / Contact Less Smart Cards
2.21 | Are all technologies available with Card + PIN reader ? |  | Yes | All Cardax reader are available with Card+ PIN
2.22 | Biometric technologies supported | Hand Geometry / Finger Print / Iris Scan / Any other (please specify) | Hand Geometry, Finger print, Iris scan etc. | Hand Geometry / Finger Print / Iris Scan
2.23 | No. of digits in PIN |  | 4 | 4 or 6
2.24 | Operator definable PIN ? | Yes / No | Yes | Yes
2.25 | No. of alarm inputs |  | 15 | Max. 240 per field controller
2.26 | Are all inputs balanced ? | Yes / No | What is the meaning of balanced inputs | Yes
2.27 | No. of relay outputs |  | 2016-04-01 | Max. 320 per field controller
2.28 | Type of communication between Controller and reader | RS232 / RS422 / RS485 / TCP/IP / Any other (pls. specify) | RS232, RS485, TTL | 2-wire RS485
2.29 | Communicaiton encrypted between Reader and Controller | Yes / No | Smart Card Readers- Encrypted | Yes
2.30 | Lock on cabinet | Yes / No | Yes | Yes
2.31 | Tamper alarm on cover opening | Yes / No | Yes | Yes. Uses optical tamper device
2.32 | Tamper alarm on controller being lifted from its mounting | Yes / No | Yes | Yes. Uses optical tamper device
2.33 | Input voltage (AC/DC, volts) |  | +/- 30 V max | 13.6 vdc +/- 15%
2.34 | Power consumption (W) |  | 1.2 W | 10 w
2.35 | IP Rating |  | IP65 | IP54
2.36 | Operating Temperature (deg C) |  | 0º to +55º C | 0 to +50 degrees C
2.37 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) | No | Yes. Refer to Deviations document
3.00 | Hand Geometry Reader
3.01 | Template Size (bytes) |  | 9 bytes | 9 bytes
3.02 | False Acceptance Rate (%) |  | The handkey can be set to a very accurate false acceptance requirements. The accuracy that can be recived will be 99.9% or better. The handkey can even receive 0.01 false acceptance rate. | 0.1
3.03 | False Rejection Rate (%) |  | The rejection can be 0.1 to 1% first try. You can allow the person to verify again and therefor almost 0 | 0.1
3.04 | Equated Error Rate (%) |  | 99.9% default. | 0.1
3.05 | Time for verification (seconds) |  | 1 second typical | Less than 1 second
3.06 | Unit memory - users | (offered ______ / expandable _______ ) | Up to 27,904 users | (offered 9,728 / expandable 32,512 )
3.07 | Unit memory - events | (offered ______ / expandable _______ ) | 3,405 buffered | (offered 5187 / expandable 5187 )
3.08 | Type of mount | Surface / Recessed / both | Table top, recessed or surface wall mount kit. | Both surfaced and recessed
3.09 | Make |  | Recognition Systems Inc. | Recognition Systems Inc.
3.10 | IP Rating |  | The reader has been tested under severe weather conditions | N/A
3.11 | Template recording and management software included | Yes / No | Yes | Included as part of the quote
3.12 | All accessories required for integration with proposed communication setup included | Yes / No | Yes | Included as part of the quote
3.13 | Operating Temperature (deg C) |  | 3º to +55º deg. C (ID3D) (The ID3DRW can work from -18º to 55º C) | Indoor model: 0 to +50 degrees C Outdoor model: -10 to +55 degrees C
3.14 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) | No | No
4.00 | Bus-mounted reader and controller
4.01 | Controller capacity - users | (offered ______ / expandable _______ ) | Offered: 2,000 Expandable:40,000 | (offered 10,000 / expandable 200,000 )
4.02 | Controller capacity - events | (offered ______ / expandable _______ ) | Offered: 1,000 Expandable:4,000 | (offered 10,000 / expandable 25,000 )
4.03 | Input voltage |  | +/- 30 V max | 13.6 vdc +/- 15%
4.04 | Input power from | Bus battery / In-built battery / both | Bus battery and in-built battery | Vehicle power system
4.05 | Separate card readers for entry and exit provided | Yes / No | Yes | Yes
4.06 | Differentiation between inward / outward trip ? |  | Yes | Yes. Time and attendance reports will indicate inward or outward trip
4.07 | Mode of wireless data transfer to on-line system |  | RF/IR | IEEE 803.11 compatible wireless LAN devices using spread spectrum frequency hopping technology
4.08 | Max. time for download of 100 events to online system and upload of 50 alterations from online system |  | 5 sec max. | 1 minute
4.09 | Is the bus required to be stationary ? If so, for how much time ? |  | Stationary for 5 seconds max. | N/A. Data transfer will commence immediately the bus comes into range of the wireless LAN access point
4.10 | Range of data transfer i.e. how far can the bus be stationed |  | 1mr.-5mr. | 500m from the wireless LAN access point
4.11 | Indication of data transfer complete ? | Yes / No | Yes | Can be achieved with minor modifications to the CardaxFT Controller
4.12 | IP Rating |  | IP65 | IP54
4.13 | All accessories required for integration with proposed communication setup included |  | Yes | Included as part of the quote
4.14 | Operating Temperature (deg C) |  | 0º to +55º C | 0 to +50 degrees C
4.15 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) | No | No
5.00 | Portable reader and controller
5.01 | Controller capacity - users | (offered ______ / expandable _______ ) | Offered: 2,000 Expandable:40,000 | (offered 10,000 / expandable 200,000 )
5.02 | Controller capacity - events | (offered ______ / expandable _______ ) | Offered: 1,200 Expandable:4,000 | (offered 10,000 / expandable 25,000 )
5.03 | Input voltage |  | +/- 30 V max | 13.6 vdc +/- 15%
5.04 | Switch for entry / exit mode provided | Yes / No / Alternative (pls. specify) | Yes | No. An entry and exit reader are provided
5.05 | Differentiation between inward / outward trip ? |  | Either an LCD display or an indication led | Yes. Time and attendance reports will indicate inward or outward trip
5.06 | Mode of data transfer to on-line system |  | RF or physical connection (hard wire) to the on line system | IEEE 803.11 compatible wireless LAN devices using spread spectrum frequency hopping technology.
5.07 | Speed of data transfer (records / second) |  | Less then 5 seconds | Max. time for download of 100 events to online system and upload of 50 alterations from online system = 1 minute
5.08 | Indication of data transfer complete ? | Yes / No | Yes | Can be achieved with minor modifications to the CardaxFT Controller
5.09 | Weatherproof ? | Yes / No | Yes | Refer to Deviations document
5.10 | Dimensions H x W x D (in mm) |  | 10X15cm. | Refer to Deviations document
5.11 | Weight of reader + controller |  | Weight – 450gr. | Refer to Deviations document
5.12 | IP Rating |  | IP65 | Refer to Deviations document
5.13 | All accessories required for integration with proposed communication setup included |  | Yes | Included as part of the quote
5.14 | Operating Temperature (deg C) |  | 0º to +55º C | 0 to +50 degrees C
5.15 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) | No | Yes. Refer to Deviations document
6.00 | Time and Attendance Readers
6.01 | Display for time, date and card number provided? | Yes / No | Yes | Yes
6.02 | Type of display | LED / LCD / Any other (pls. specify) | LCD display | Multi-line, backlit dot matrix LCD display
6.03 | In-built or separate unit |  | Either one in-built unit with two separate readers or one in-built unit including one reader + a separate reader | In-built
6.04 | If separate, combined unit for both card readers ? | Yes / No |  | N/A
6.05 | Capable of using existing Cat 5 cable from current reader locations to PIB ? | Yes / No | Yes | Yes
6.06 | IP Rating of readers |  | IP 65 | IP56 with additional cover
6.07 | IP Rating of display |  | IP 55 | IP56 with additional cover
6.08 | Operating Temperature (deg C) |  | -10 | 0 to +50 degrees C
6.09 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) | No | Yes. Refer to Deviations document
7.00 | Proximity / Smart Cards
7.01 | ISO thickness ? | Yes / No | Yes | SmartCard: Yes Proximity: No
7.02 | Which out of the following options are available (a) direct on-card printing (b) printing on label and sticking on card (c) separate card printed and attached to access card |  | Direct on card printing | SmartCard: (a), (b) Proximity: (b)
7.03 | Operating Temperature (deg C) |  | Contact less smart card: IP65 –20º to +85º C | 0 to +50 degrees C
7.04 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) | No | Yes. Refer to Deviations document
8.00 | Proximity / Smart Card Reader
8.01 | Read range |  | Smart card reader- up to 15cm. | SmartProx (no pinpad): 100 mm SmartProx (with pinpad): 100 mm SmartCard (no pinpad): 5 mm SmartCard (with pinpad): 15 mm
8.02 | Is the communication between reader and card encrypted ? | Yes / No | Smart card- Encrypted. | Yes
8.03 | Will mounting the reader directly on metal affect the read range ? | Yes / No | Yes | Yes. Approximately 10% reduction
8.04 | Available in Card + PIN mode ? | Yes / No | Yes | Yes (both technologies)
8.05 | IP Rating |  | IP 65 | IP54 (both technologies) IP56 with additional cover
8.06 | Make |  | Contact less smart cards readers – OTI | Cardax
8.07 | Operating Temperature (deg C) |  | 0º to +85ºC for smart cards readers | SmartProx: -10 to +55 degrees C SmartCard: 0 to +50 degrees C
8.08 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) | No | Yes. Refer to Deviations document
9.00 | Card Encoder with software
9.01 | Encoder available for Proximity Cards | Yes / No | Yes | Yes
9.02 | Unique facility code option for RPL available for both Proximity and Smart Card | Yes / No | Yes | Yes
9.03 | Capable of encoding 9 digit card number apart from facility code | Yes / No | Yes | Yes
9.04 | Maintains detailed record of all encoding events ? | Yes / No | Yes | Yes
9.05 | Hardware lock on workstation using encoder software | Yes / No | Yes | Yes
9.06 | Operating Temperature (deg C) |  | 4-65 | 0 to +50 degrees C
9.07 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) | No | No
10.00 | Electromagnetic Lock
10.01 | Holding force (N) |  | 5000N
10.02 | Locked / unlocked status monitored ? | Yes / No | Yes
10.03 | Input voltage range |  | 12V DC – 24V DC
10.04 | Make |  | Eff Eff / Yale
10.05 | Certifications / Approvals | UL / CE / Any other | UL
10.06 | Make |  | Eff Eff / Yale
10.07 | Operating Temperature (deg C) |  | 0º to +65º C
10.08 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) | No
11.00 | Turnstile
11.01 | Grade of stainless steel |  | 304 Electro Polished
11.02 | Rotor arms | 4 x 90 deg. / 3 x 120 deg. | Stainless steel
11.03 | Fail-safe / fail-secure option settable for either direction on-site ? |  | Yes
11.04 | Drive | Hand operated / Torque motor | Torque motor
11.05 | Open / locked status output ? | Yes / No | Yes
11.06 | IP Rating |  | IP65
11.07 | Make |  | Tomsed
11.08 | Operating Temperature (deg C) |  | -20º to +65º C
11.09 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify) | No

## Security Control Room
Sl.No. | Technical feature | Equipment offered
1.00 | Matrix Switcher
1.01 | Number of cameras | Offered ____ / Expandable ____
1.02 | Number of monitors | Offered ____ / Expandable ____
1.03 | Number of keyboards | Offered ____ / Expandable ____
1.04 | Alarm inputs | Offered ____ / Expandable ____
1.05 | Alarm outputs | Offered ____ / Expandable ____
1.06 | Number of presets | Offered ____ / Expandable ____
1.07 | Number of "tours" | Offered ____ / Expandable ____
1.08 | Can the presets be triggered using a software (ASCII ?) command ? If yes, please give details of system offered.
1.09 | Keyboard with in-built joystick | Yes / No
1.10 | Backup CPU offered | Yes / No
1.11 | In-built floppy disk drive to load setup | Yes / No
1.12 | Macro recording, give details of number of macros definable and number of steps in each
1.13 | Make
1.14 | Certifications / Approvals | UL / CE / Any other
1.15 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify)
2.00 | Video Motion Detection System
2.01 | Max. no. of cameras | Offered ____ / Expandable ____
2.02 | Max. no. of cells in each view from which alarm zones can be selected
2.03 | No. of alarm zones per camera
2.04 | Does it take care of perspective i.e. differentiate between near and far objects | Yes / No
2.05 | Alarm on camera blocking | Yes / No
2.06 | Max. no. of alarm frames stored on hard disk
2.07 | Make
2.08 | Certifications / Approvals | UL / CE / Any other
2.09 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify)
3.00 | Large Screen Display
3.01 | Technology offered (give details)
3.02 | Diagonal size of screen (mm)
3.03 | Angle of view - horizontal (degrees)
3.04 | Angle of view - vertical (degrees)
3.05 | Depth required (in mm - from front of screen to the wall behind the unit)
3.06 | Outer dimensions H x W x D (in mm)
3.07 | Continuous duty ? | Yes / No
3.08 | Life of lamp or any such item that requires frequent replacement (hours)
3.09 | Availability of 43" Plasma Display Monitors ? | Yes / No
3.10 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify)
4.00 | Access Control Server with mirror backup
4.01 | Changeover from main server to backup server | Manual / Automated
4.02 | Time taken for changeover (seconds)
4.03 | Possibility of data loss during changeover | Yes / No
4.04 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify)
5.00 | Photo-ID Card Making System
5.01 | Uses same database as main Access Control system ? | Yes / No
5.02 | Modes of image capture | From file / scanner / live camera / any other
5.03 | Log of all cards printed ? | Yes / No
5.04 | Capability to overlay a 25 mil thick laminate over card | Yes / No
5.05 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify)
6.00 | Time Lapse Recorder
6.01 | S-VHS option | Yes / No
6.02 | Is a Real-Time recorder available that offers 8 hours of recording time ? | Yes / No
6.03 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify)
7.00 | CCTV Monitors
7.01 | Resolution (horizontal TV lines)
7.02 | Flat picture tube | Yes / No
7.03 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify)
8.00 | Video Multiplexers
8.01 | S-VHS monitor output | Yes / No
8.02 | Full duplex | Yes / No
8.03 | Display Image memory (MB)
8.04 | Alarm inputs available for each camera | Yes / No
8.05 | Digital image size (full screen, no. of pixels H x V)
8.06 | Deviations from specifications in Tender no. 1J-JC 0003 | No / Yes (please specify)